	To:  Nutrient Control
	[image: image1.jpg]SHS




S & S Electric Motors, Inc.

125 Falling Spring Road

Chambersburg, PA  17202
Ph 717-263-1919

Fax 717-263-7351



	
	

	Date: 12/4/2023
From: Jenny Sollenberger         
	


In regards to the 15KW Criman mixer (your PO# 9259-LFS):
Hipot/meg/surge test windings-OK. Windings covered in oil indicating seal failed at the gearbox. Steam & bake windings and replace dirty bearings.
Total Cost: $297.00

Thank you!

Jenny Sollenberger

S&S Electric Motors, Inc.

717-263-1919

